## HeatCalc
Directions:
1 | Enter or modify information in the |  |  | blue | cells only. All other cells are locked.
2 | DO NOT enter both R and U values. The worksheet defaults to the R value. If you want to use the U value, leave the R value empty.
3 | The values listed in the R and U columns are the most common but may be modified depending on building materials actually used.
4 | For all Areas, enter the value in square feet. BTU/hr means British Thermal Unit per hour, a unit measure of heat loss over time.
5 | The Areas in Row 5A and 5C are locked for your benefit. Please insure that these are a positive number or you will get an error message.
6 | For further direction, cells with a red triangle offer additional comments when the cursor is placed over the cell.
7 | When finished, print this form and attach it to your plans for review.
Pikes Peak Regional Building Department
Heat Loss Calculation Table (ver. 2.2)
Contractor/Builder: | [6 empty] | Address or Master#: | [6 empty] | Date:
1 | Space under consideration | [5 empty] | Crawlspace |  | Basement |  | Main Floor |  | Upper Floor |  | Entire House
2 | Running perimeter of exterior wall (feet) | [13 empty] | 0
3 | Floor area (square feet) | [13 empty] | 0
4 | Wall height (feet) | [13 empty] | 0
TYPE OF EXPOSURE |  | Material |  | R | U | T | Area | BTU/hr | Area | BTU/hr | Area | BTU/hr | Area | BTU/hr | Area | BTU/hr
5 | Net exposed walls | A. | Concrete earth | 10 |  | 25 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  | B. | Concrete air | 10 |  | 72 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
|  | C. | 2x4 | 18 |  | 72 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | D. | 2x6 | 20 |  | 72 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
6 | Windows and Glass doors | E. | Window bsmt |  | 0.32 | 72 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
|  | F. | Window other |  | 0.32 | 72 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
|  | G. | Glass door |  | 0.32 | 72 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
7 | Solid doors | H. |  |  | 0.32 | 72 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
8 | Gross roof | I. | Flat ceiling | 49 |  | 72 |  |  |  | 0 |  | 0 |  | 0 | 0 | 0
| Skylights | J. |  |  | 0.55 | 72 |  |  |  | 0 |  | 0 |  | 0 | 0 | 0
8a | Gross roof | Ia. | Sloped ceiling | 49 |  | 72 |  |  |  | 0 |  | 0 |  | 0 | 0 | 0
Pitch in 12
| Skylights | Ja. |  |  | 0.55 | 72 |  |  |  | 0 |  | 0 |  | 0 | 0 | 0
9 | Floors on grade | K. | Slab insulation | 10 |  | 25 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
10 | Floors / unheated | L. |  | 30 |  | 72 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
11 | Floors / exterior | M. |  | 30 |  | 72 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
12 | Building Envelope Heat Loss | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0
13 | Infiltration Heat Loss (based on average of 0.35 ACH) | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0
14 | Total Heat Loss | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0
15 | Altitude deration | Caloric deration of natural gas |  |  |  |  | Output |  | Output |  | Output |  | Output |  | Total Output
|  | (constant) |  |  | 80% |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
16 | Efficiency deration | Efficiency of heating equipment |  |  |  |  | Input |  | Input |  | Input |  | Input |  | Total Input
[5 empty] | 80% |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
-
NO ROOF CALCULATED | [14 empty] | form release: 12/09/2003
- | [14 empty] | revised 10/25/2011
Note on B17: Enter the average wall height for each story measured from floor surface of one floor to the floor surface of the floor above.
Note on B26: Include any doors than have less than 50% glazing.
Note on B27: Assumes insulation at the ceiling joist or bottom chord of trusses. Enter the flat area of the entire roof, including any skylights.
Note on B29: Assumes rafter or scissor truss construction. Enter the flat area of the entire roof, including any skylights. Pitch is taken into account in the next row.
Note on B30: Enter the pitch of the INTERIOR surface of a cathedral or vaulted ceiling. This is the vertical RISE for a horizontal RUN of 12.
Note on B32: Enter the area of insulation for the foundation wall below exposed full-height framed wall. Examples include: walk out basements and slab on grade construction.
Note on B33: These include: Garages, crawlspaces and similar construction where the floor is over unheated but enclosed construction.
Note on B34: These include: Bays, porches, overhangs, cantilevers and similar construction where the floor is exposed to the exterior.
Note on D19: The foundation wall surface area that is in contact with soil. Calculated for you.
Note on D20: Enter the foundation wall surface area in contact with outside air.
Note on F41: This information is usually listed on the appliance, or available from the supplier. This value cannot be lower than 80%.
Note on H17: For crawlspaces, enter the height from grade to the top of the floor above.
Note on H19: These cells are locked in order to verify proper sum of areas. If you get a negative number, your areas do not match the perimeter times wall height.
Note on I27: A crawlspace does not have a roof, it has a floor over it. Enter any floor insulation values in the appropriate level containing the floor.
Note on J19: These cells are locked in order to verify proper sum of areas. If you get a negative number, your areas do not match the perimeter times wall height.
Note on L21: These cells are locked in order to verify proper sum of areas. If you get a negative number, your areas do not match the perimeter times wall height.
Note on N21: These cells are locked in order to verify proper sum of areas. If you get a negative number, your areas do not match the perimeter times wall height.
Note on P35: This is the summary that should appear on the Heat Loss Certificate.
Note on P41: This is the minimum heat input required to meet the heat loss as calculated.